|  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **TEST REPORT** | | | | | | | | | | | | | |
|  | | | | | | | | | | | | | |
| **Purpose: To Determine the Average air Velocity & Air Changes per Hour at the work location in a clean room or clean air device** | | | | | | | | | | | | | |
| Client Ref no  Area of Test | M/s Shasun Pharmaceuticals Ltd.  AWS/ACPH/SPL/001  Packing Section - I | | | | | Plant  Date of Test AHU Number | | | | | Cuddalore  03.12.2013  AHU-01 | | |
| **Instrument Used** | | | | | | | | | | | | | |
| Instrument Serial Number  Calibrated on | Hot Wire Anemometer Q588201  25-Jan-13 | | | | | Make Model  Calibration Due on | | | | | LUTRON AM-4204  24-Jan-14 | | |
| **Obtained Test Results** | | | | | | | | | | | | | |
| Room Name / Number | Design ACPH | Grill/Filter Reference No. | Filter oc Area | ity Reading in FPM | | | | | Avg Velocity FPM | Air Flow CFM | Total Air Flow CFM | Room Volume CFT | Air Changes per Hour |
| Sqft. | 1 | 2 | 3 | 4 | 5 |
| RCVD - 3 | NLT 20 | S5 | 0.62 | 1325 | 1241 | 1255 | 1236 | 1244 | 1260 | 781 | 2312 | 3388 | 41 |
|  | | | | | | | | | | | | | |
| **Inference:** | The above test Confirms the Air flow Velocity and Air Changes per Hour as per the specified requirement | | | | | | | | | | | | |
|  | | | | | | | | | | | | | |
| **Test Conducted By** | |  | **Test Verified By** | | | | | | | | | | |
| For Airwin Services | | | For Shasun Pharmaceuticals Ltd. | | | | | | | | | | |